## Cover_Sheet
MicrogridCreator (MgC) input sheet
Background: | MgC is a tool that supports planners and operators of microgrids / decentralized energy systems in the design phase of the project. The usage of the MgC is not restricted to only new installations, but is meant for system expansion as well. Our tool calculates the best system setup (i.e. the optimal combination of available technologies, their size, and operation), achieving the highest KPI scores, within the given technical and economical frame.
Scope: | Technologies: This Excel sheet contains information and parameters for several technologies, that we can currently simulate in our tool. Different technology can be selected, by means of drop down lists, marked in green. Each technology consists of a set of economical and technical parameters. Once a specific technology is selected, all pertinent fields will be automaticaly filled with default values from the case study. The user can manually edit any field to input custom data. Extra technologies can be added, by simply copying existing columns and pasting them in blank ones. Note: For the parameters "OPEX (w/o fuel)" and "Self discharging ratio" the unit "€/a" was included as default. Those units can be changed at once via the dedicated drop-down list. Whenever the user wants to include custom values for certaing fields, he/she should also provide the required unit, if this is different from the default one. Resources: This sheet contains data related to the costs of different resources, including electricity tariffs. As in the case of "Tecnologies", default values are provided, where suitable.
Legend: |  | Select the desired item from the drop down list
| - | Leave those cells empty
| Preferred currency | € | Note: All the default values are available in EUR only
Disclaimer: | Please be aware that this file includes just a small fraction of the input parameters that can be input into the MgC. For user convenience, we will undergo some assumptions while processing the data he input in the sheet.

## Technologies
Technology |  |  | Generator - GN | Photovoltaic System - PV | Wind Turbine - WT | Lead Acid Battery - B2 | Select
Economical parameters |  | Unit
CAPEX | unit |  | €/kW | €/kW | €/kW | €/kWh | N/A
| value |  | 300 | 1000 | 900 | 150 | N/A
OPEX (w/o fuel) |  | €/a | 24.6 | 64 | 30 | 13 | N/A
Estimated life time |  | a | 20 | 20 | 20 | 13 | N/A
Financing | debt share | – | 0 | 0 | 0 | 0 | N/A
| debt term | a | 15 | 15 | 15 | 10 | N/A
Technical parameters
Nominal capacity (electrical or thermal) | unit |  | kW | kW | kW | kWh | N/A
| maximum value |  | 1000 | 1000 | 1000 | 1000 | N/A
| minimum value | kW | 0 | 0 | 0 | 0 | N/A
Operational power | minimum value | kW | 0.4 | - | - | 0.5 | N/A
Conversion efficiency | Conversion to electrical power | % | 35 | 15.67 | 29 | - | N/A
| Conversion to thermal power | [–] (COP,EER) | - | - | - | - | N/A
Maximum power gradient |  | 1/h | 12 | - | - | 1 | N/A
Advanced Parameters
Storage
Self discharging ratio |  | 1/d | - | - | - | 0.3506% | N/A
Minimum SOC |  | % | - | - | - | 50 | N/A
Rountrip efficiency |  | % | - | - | - | 80 | N/A
Heat loss |  | kW/h | - | - | - | - | N/A
PV system
Efficiency | Efficiency loss, temperature-dependent | %/K | - | 0.38 | - | - | N/A
| Inverter efficiency (Euro efficiency) | % | - | 95.3 | - | - | N/A
Wind turbine
Wind speed | Start-up wind speed | m/s | - | - | 2.5 | - | N/A
| Rated wind speed | m/s | - | - | 10 | - | N/A
Cumulative rotor radius |  | m | - | - | 2.99 | - | N/A

## Hide (hidden)
Economical parameters
Type | Spec |  | Generator - GN | Fuel Cell System - FC | Motoric CHP System - MC | Heat Pump - HP | Electric Heater - EH | Compression Chiller - CC | Heating Boiler - HB | Type | Spec |  | Li-ion Battery - B1 | Lead Acid Battery - B2 | Heat Storage - HS | Cooling Storage - CS | Type | Spec |  | Photovoltaic System - PV | Wind Turbine - WT
|  |  | €/kW | €/kW | €/kW | €/kW | €/kW | €/kW | €/kW |  |  |  | €/kWh | €/kWh | €/kWh | €/kWh |  |  |  | €/kW | €/kW
Fixed cost | Size specific investment cost (incl. installation) | [€/kW] | 300 | 3000 | 700 | 310 | 20 | 150 | 45 | Fixed cost | Size specific investment cost (incl. installation) | [€/kWh] | 600 | 150 | 10.58 | 20 | Fixed cost | Size specific investment cost (incl. installation) | [€/kW] | 1000 | 900
Fixed cost | General OMC | [€/a] | 24.6 | 240 | 260 | 114 | 6 | 160 | 100 | Fixed cost | General OMC | [€/a] | 24 | 13 | 25.06 | 38.8 | Fixed cost | General OMC | [€/a] | 64 | 30
Fixed cost | Size specific OMC | [€/(kW a)] | 6 | 60 | 14 | 6.2 | 0.4 | 3 | 0.9 | Fixed cost | Size specific OMC | [€/(kW a)] | 12 | 3 | 0.21 | 0.4 | Fixed cost | Size specific OMC | [€/(kW a)] | 80 | 18
Variable cost | Use specific OMC | [€/h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Variable cost | Variable OMC |  | - | - | - | - | Variable cost | Use specific OMC | [€/h] | 0 | 0
Durability | Technical lifetime | [a] | 20 | 5 | 25 | 20 | 25 | 20 | 25 | Durability | Technical lifetime | [a] | 10 | 13 | 25 | 20 | Durability | Technical lifetime | [a] | 20 | 20
Financing | Debt share | [–] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Financing | Debt share | [–] | 0 | 0 | 0 | 0 | Financing | Debt share | [–] | 0 | 0
Financing | Debt term | [a] | 15 | 4 | 19 | 15 | 19 | 15 | 19 | Financing | Debt term | [a] | 8 | 10 | 19 | 15 | Financing | Debt term | [a] | 15 | 15
Technical parameters
General parameters
|  |  | kW | kW | kW | kW | kW | kW | kW |  |  |  | kWh | kWh | kWh | kWh |  |  |  | kW | kW
Maximum capacity | Electric power/Thermal power | [kW] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | Maximum capacity | Storage capacity | [kWh] | 1000 | 1000 | 1000 | 1000 | Maximum capacity | Electric power | [kW] | 1000 | 1000
Minimum installable capacity | Main power type | [kW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Minimum installable capacity | Storage capacity | [kWh] | 0 | 0 | 0 | 0 | Minimum installable capacity | Electric power | [kW] | 0 | 0
Minimum capacity | Electric power (relative to max) | [–] | 0.4 | 0.4 | 0.2 | 0.25 | 0 | 0.25 | 0.5 | Minimum capacity | Storage capacity (relative to max) | [–] | 0.1 | 0.5 | 0.033 | 0.058 | Relative minimum capacity |  |  | - | -
Conversion efficiency | Conversion to electrical power | % | 35 | 50 | 34.1 | - | - | - | - | Conversion efficiency | Charging | [–] | - | - | - | - | Conversion efficiency | Conversion to electrical power | [–] | 15.67 | 29
Conversion efficiency | Conversion to thermal power | [–] (COP,EER) | - | 0.25 | 0.488 | 3 | 0.999 | 3 | 0.95 | Conversion efficiency | Discharging | [–] | - | - | - | - | Conversion efficiency |  |  | - | -
Maximum power gradient | Max power gradient upwards | [1/h] | 12 | 0.5 | 12 | 1 | 10 | 1 | 1 | Maximum power gradient | Max power gradient charging | [1/h] | 0.6 | 1 | 2 | 2 | Maximum power gradient |  |  | - | -
Specific parameters
Storage
Storing efficiency | Storing loss per hour | [1/h] | - | - | - | - | - | - | - | Storing efficiency | Storing loss per hour | [1/h] | 3.4766e-06 | 0.00014632 | 0.00079 | 0.00096224 |  |  |  | - | -
Storing efficiency | Storing loss per day | [1/d] | - | - | - | - | - | - | - | Storing efficiency | Storing loss per day | [1/d] | 0.008343% | 0.3506% | 1.87% | 2.284% |  |  |  | - | -
Storing efficiency | Storing loss per month | [1/30d] | - | - | - | - | - | - | - | Storing efficiency | Storing loss per month | [1/30d] | 0.25% | 10% | 43% | 50% |  |  |  | - | -
Storing efficiency | Heat loss | kW/h | - | - | - | - | - | - | - | Storing efficiency | Heat loss | kW/h | - | - | 0.11 | - |  |  |  | - | -
Minimum SOC |  | % | - | - | - | - | - | - | - |  |  |  | 10 | 50 | - | - |  |  |  | - | -
Rountrip efficiency |  | % | - | - | - | - | - | - | - |  |  |  | 90 | 80 | 99.99 | 99.99 |  |  |  | - | -
Usable energy | Energy density | [kWh/m3] | - | - | - | - | - | - | - | Usable energy | Energy density | [kWh/m3] | #REF! | #REF! | #REF! | #REF! |  |  |  | - | -
Efficiency loss, temperature-dependent | [1/K] |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | Efficiency loss, temperature-dependent | [%/K] | 0.38 | -
Inverter efficiency (Euro efficiency) | [–] |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | Inverter efficiency (Euro efficiency) | [%] | 95.3 | -
Start-up wind speed | [m/s] |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | Start-up wind speed | [m/s] | - | 2.5
Rated wind speed | [m/s] |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | Rated wind speed | [m/s] | - | 10
Cumulative rotor radius | [m] |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | Cumulative rotor radius | [m] | - | 2.99
|  | === Dispatchable technologies === | === Cost === | €/a |  | Cost | [7 empty] | Income
|  | Generator - GN | Electricity, fixed tariff - EF | €/(kW a) |  |  |  |  | Electricity, fixed tariff - EF | Electricity, variable tariff - EV | Natural Gas - NG | Fuel Oil - FO | Diesel - DI | Solar Power Generation - PV | Wind Power Generation - WT | Co-generation (CHP) - CG
|  | Fuel Cell System - FC | Electricity, variable tariff - EV | €/a |  | Demand rate | Demand rate, size specific | €/kWh/a | 0 | 0 | 0 | 0 | 0 | - | - | -
|  | Heat Pump - HP | Natural Gas - NG | % CAPEX |  | kWh-rate | kWh-rate, peak | €/kWh | 0.28 | 0.29 | 0.05 | 0.045 | 0.1 | - | - | -
|  | Motoric CHP System - MC | Fuel Oil - FO | 1/h |  | kWh-rate | kWh-rate,non- peak | €/kWh | - | 0.25 | - | - | - | - | - | -
|  | Electric Heater - EH | Diesel - DI | 1/d |  | kWh-rate time | Peak time in | h | - | 6 | - | - | - | - | - | -
|  | Heating Boiler - HB | === Resources - Income === | 1/30d |  | kWh-rate time | Peak time out | h | - | 22 | - | - | - | - | - | -
|  | Compression Chiller - CC | Solar Power Generation - PV |  |  | Feed-in | kWh-rate | €/kWh | - | - | - | - | - | 0.12 | 0.08 | 0.08
|  | === Storage === | Wind Power Generation - WT
|  | Li-ion Battery - B1 | Co-generation (CHP) - CG
|  | Lead Acid Battery - B2 | === Revenues ===
|  | Cooling Storage - CS | Solar Power Generation - PV
|  | Heat Storage - HS | Wind Power Generation - WT
|  | === Renewable sources === | Co-generation (CHP) - CG
Photovoltaic System - PV
Wind Turbine - WT
Select

## Resources
|  |  | Diesel - DI | Electricity, fixed tariff - EF | Electricity, variable tariff - EV | === Resources - Income ===
Demand rate | Demand rate, size specific | €/kWh/a | 0 | 0 | 0 | N/A
kWh-rate | kWh-rate, peak hours | €/kWh | 0.1 | 0.28 | 0.29 | N/A
kWh-rate | kWh-rate, off-peak | €/kWh | - | - | 0.25 | N/A
kWh-rate time | Peak time starts at | h | - | - | 6 | N/A
kWh-rate time | Peak time finishes at | h | - | - | 22 | N/A
Feed-in | kWh-rate | €/kWh | - | - | - | N/A